# Transformer Data Sheet: (Circled items are specific to this project.)

Customer Name: _______________________Project/Quotation Number: ___________ Item No.___

3 ( KVA Rating:		750	1000	1500	2000	2500	3000	3750	5000	7500	10000				OTHER (_______)

1( KVA Rating:		500	750	833 	1250	1667	2500	3333	6667	Other (_____)

Frequency:	50 HZ	60 HZ

Impedance:	ANSI C57.12.10 Standard 	Other (______)

Winding Temperature Rise: 	65 (C (Standard)	55 (C		55/65 (C

Primary Voltage: (KV)	4.16	12.47	13.2	13.8	14.4	22.9	34.4	43.8	67 					OTHER (_______)

Primary Taps:	Standard (( 2-2 ½) 	OTHER (__________)

Primary BIL: (KV)	45	60	75	95	110	150	200	250	350

Primary Connection:	Delta	Wye

Primary Termination:	Switchgear throat		Air Terminal Chamber 	Cover Bushing

Primary Location:	Standard	 ____	ANSI Segment	1__	2 __	3 __	4 __

Secondary Voltage: (KV)	0.480	2.4	4.16	7.2	8.32	12.47	13.8	14.4	22.9	34.4 OTHER (_______)

# Secondary BIL:  (KV)	45	60	75	95	110	150	200

Secondary Connection: 	Delta	Wye

Secondary Termination: 	 	Switchgear throat	 __	Air Terminal Chamber__	Cover Bushings__

Secondary Location:	Standard ____	ANSI Segment	1 __	2 __	3__	4 __

Secondary Termination Location:	Right		Left

Insulating Fluid:	 	Mineral oil	Silcone fluid	R-Temp

Application Location:	Indoor		Outdoor

Forced Air Rating:	OA/FA		OA/Future FA		OTHER (_______)

Sound Level: 	Standard 	Special ________

Special Tests:	Witness	__;	Temperature __	;	Impulse QC __ 	ANSI __;	Sound __;	OTHER (___________)

Other Special Instructions:  ________________________________________________________________________

______________________________________________________________________________________

______________________________________________________________________________________

______________________________________________________________________________________

______________________________________________________________________________________

______________________________________________________________________________________

______________________________________________________________________________________

______________________________________________________________________________________________

LIQUID-FILLED SUBSTATION TRANSFORMERS

WITHOUT LOAD TAPCHANGER

SPECIFICATION  PS1001S

1.0	SCOPE

  - The ABB Power T&D Company {power} {distribution} substation transformer design is the basis for specification. Other approved manufacturers are ______________________ ____________________________.

  - This specification together with the applicable Transformer Data Sheet provides the technical requirements for the design, manufacture and test of substation transformers.

  - The service conditions shall be as specified in Usual Service Conditions section of C57.12.00, unless otherwise modified on Transformer Data Sheet.

  - This specification covers only the general requirements of the transformer. The specific requirements are detailed on the Transformer Data Sheet.

- CODES AND STANDARDS

  - All codes and standards referenced in this specification shall be those in effect at the time of Purchase Order award. Deviations from this specification and referenced codes and standards shall be obtained in writing from Buyer.

    - ANSI/IEEE C57.12.00, Distribution, Power, and Regulating Transformers, General Requirements for Liquid-Immersed ……

    - ANSI C57.12.10, American National Standard for Transformers 230 kV and Below ………..

    - ANSI/IEEE C57.12.90, Test Code for Liquid-Immersed Distribution, Power and Regulating Transformers and Guide for Short-Circuit Testing of Distribution and Power Transformers

    - ANSI/IEEE C57.98, Impulse Tests, Guide for Transformer (Appendix to ANSI/IEEE C57.12.90)

    - ANSI/NFPA 70, National Electrical Code

    - ASTM D877 - Test Method for Dielectric Breakdown Voltage of Insulating Liquids Using …….

  - It shall be the Seller’s responsibility to be, or to become, knowledgeable of the requirements of these Codes and Standards. Any required changes or alterations to the equipment to meet the Codes and Standards requirements shall be at the expense of the Seller.

  - Equipment proposed by the Seller that cannot fully meet the requirements of this specification shall have all exceptions clearly stated in the proposal. No exception shall be allowed, unless approved by the Buyer in writing.

- QUALITY ASSURANCE

  - The manufacturer shall have specialized in the design, manufacture and assembly of liquid filled secondary substation transformers for a minimum of {25} years. The transformer manufacturer and location of manufacture and test are to be supplied at the time of quotation.

  - The manufacturer shall a well documented quality assurance program, which includes procedures for all activities in order entry, design, material procurement, manufacturing processes, testing, shipping and post shipment product follow.

  - The test facility used to perform loss tests in accordance with ANSI C57.12.90 must be certified by an approved 3rd party to meet NBS 1204 standards for accuracy.  Calibration of the equipment used for these loss measurements must be traceable to NIST or an approved equal 3rd party laboratory. Records of all equipment calibration shall be made available to the Buyer upon request.

  - The transformers shall be manufactured by a company which is certified to ISO 9001:1994, EN ISO 9001:1994; BS EN ISO 9001:1994; ANSI/ASQC Q9001: 1994 for design and manufacture of Power, Distribution and Specialty Dry Type Transformers.  A certificate of Compliance to this requirement shall be provided with the proposal.

- TRANSFORMER TECHNICAL REQUIREMENTS

  - Winding Characteristics

    - All windings and internal connections shall be {copper} {aluminum}.

    - The windings shall be tightly wound utilizing tension devices to place the conductor into the coils.

    - For optimum dielectric and mechanical strength, a minimum of two sheets of epoxy coated thermally upgraded Insuldur( insulation shall be placed between each layer in the winding.

    - Sheet conductor shall be used in secondary winding to minimize vertical short circuit forces.

    - The transformer shall be designed and constructed to be completely self protected by its ability to withstand the external short-circuits, as defined by ANSI C57. 12.00 and tested in accordance with C57.12.90.

    - Evidence of compliance to the short-circuit requirements shall be available to the Buyer at the time of quotation.

    - The transformer design shall be capable of operating above rated voltage or below rated frequency in accordance with ANSI C57.12.00.

  - Sound Level

    - The substation transformer and auxiliary cooling equipment shall be designed and constructed to minimize the audible noise generated with the transformer energized at rated voltage and with all auxiliary cooling equipment in operation. The acceptable noise level shall be in accordance with NEMA TR 1. The measurement procedure shall be as specified in ANSI C57.12.90.

  - Bushings

    - High voltage and low voltage bushings shall be furnished with the ratings shown on the Transformer Data Sheet.

    - The bushings above 600-volt rating shall be gray wet-process porcelain. The location shall be as indicated on the Transformer Data Sheet.

  - Core

    - The core and coil shall be clamped and braced using a six piece welded construction to resist coil movement and to prevent the shifting of core laminations caused by short-circuit events.

    - The core shall be constructed of high-grade, grain oriented, silicon steel laminations, with high magnetic permeability. Magnetic flux density is to be kept well below the saturation point. The core construction shall include step-lap mitered joints to keep core losses, excitation current and noise level to a minimum.

  - De-Energized Tap Changer

    - A manually operated de-energized tap changer shall be provided for changing the off circuit taps.

    - Full capacity taps shall be located in the high voltage windings and shall be in accordance with the Transformer Data Sheet.

    - The tap changer shall be capable of carrying the full transformer short-circuit current without damage or contact separation.

    - The tap changer shall be gang operated from a single operating point and shall have an easily visible position indicator.

    - The tap changer operating mechanism shall include provisions for pad locking in each tap position.

  - Arrestors

    - The primary side requirements are: {provisions for} __ kV {distribution} {intermediate} {station} class arrestors. The arrestor mounting location shall be in close proximity to the primary bushings.

    - The secondary side requirements are: {provisions for} __ kV {distribution} {intermediate} {station} class arrestors. The arrestor mounting location shall be in close proximity to the secondary bushings.

  - Insulating Fluid And Preservation System

    - The fluid preservation system shall be a sealed tank type.

    - The insulating fluid shall be {mineral oil} {Silicone fluid} {high molecular weight hydrocarbon fluid}.

    - The transformer insulating fluid shall be certified to contain no detectable PCB’s at the time of shipment and the tank shall be so labeled. Certification shall also be provided that the transformer and components have not been contaminated with PCB’s prior to shipment.

    - The transformer insulating fluid shall meet or exceed the requirements of the appropriate ANSI and ASTM fluid Standards. The transformer fluid shall be tested for dielectric breakdown and moisture content just prior to the time of shipment.

  - Tank Design

    - The transformer tank, cooling equipment and compartments subject to operating pressures shall be designed for full vacuum, without permanent deformation. The maximum design withstand pressure shall be indicated on the nameplate.

    - Tank design shall include sufficient expansion volume to allow operation under specified load conditions.

    - The main cover shall be of welded onto the tank.

    - One or more bolted-on handholes shall be provided in the tank cover for access to bushing connections and current transformers, when required. The opening shall be of sufficient size to allow removal of any CTs.

    - The transformer base shall be suitable for rolling or skidding in the direction of either tank base centerline.

    - The base shall be designed so the center of gravity of the transformer as assembled for transport does not fall outside the base for a tilt of fifteen degrees.

    - Lifting lugs shall be provided at each corner of the tank. The lifting lugs shall be designed to provide a minimum safety factor of 5.

    - Jacking pads or bosses shall be provided.

    - Pulling provisions, for towing the transformer parallel to either centerline, shall be provided.

  - Gaskets

    - The gaskets shall be compatible for the insulating fluid in the transformer tank.

    - Gasket in contact with Silicone fluid or vapors shall be Viton material.

    - Metal surfaces to which gaskets are applied shall be smooth, and shall have sufficient rigidity to assure proper compression of the gaskets.

  - Cooling System

    - The transformer cooling system shall be as specified on the Transformer Data Sheet.

    - Cooling tubes or radiators shall be rigidly supported to the tank wall, either through pipes or brackets.

    - When fans are required, the fan assembly shall have low noise level, not to exceed the required sound level as specified in NEMA TR-1. The voltage supply for the fan motor(s) shall be 240 volts.

  - Grounding Provisions

    - All non-energized metallic components of the transformer shall be grounded.

    - Tank grounding provisions shall consist of two ground pads, welded to the base or to the tank wall near the base on diagonal corners.

    - The ground pads shall be copper-faced or stainless steel with two holes spaced horizontally at 1.75-inch centers and tapped for 0.5 inch 13-UNC tread.

  - Accessories

    - The transformer shall be equipped with a complete set of accessories, as per ANSI C57.12.10.

4.11.2	Optional accessories

- {Winding hot-spot temperature indicator with alarm contacts.}

- {Mechanical relief device {with alarm contacts}}.

- {Alarm Contacts for {__} Liquid Level Gauge; {__} Liquid Temperature Indicator; {__} Pressure Vacuum Gauge}.

- {A rapid pressure rise relay with seal-in relay contacts and controls mounted in a control wiring cabinet. The operating voltage shall be {115 ac} {230 ac} {24 dc} {48 dc} {125 dc} {240 dc}}.

- {A space heater {with thermostat} shall be provided in the control cabinet.}

  - The control cabinet shall be NEMA Type 4X. The cabinet door shall have provisions for padlocking.

  - Wiring

    - All devices mounted on the transformer, including current transformer secondary circuits, shall be wired to the control cabinet.

    - All control wiring shall be a minimum of #14 AWG SIS and #12 AWG for current transformers. Wiring between gauges and the control box can be #14 AWG SO cable.

    - Wiring shall be terminated with a ring-type insulated compression lug.

    - Current transformer terminal blocks shall be the shorting type.

    - Each wire shall be identified with a wire marker.

  - Nameplates

    - Transformer shall be furnished with a non-corrosive diagrammatic nameplate, permanently attached with non-corrosive hardware.  The diagrammatic nameplate shall include the name of the manufacturer of the equipment as well as the location where the transformer was manufactured and tested.

    - The nameplate shall contain all connection and rating information in accordance with ANSI C57.12.00 nameplate type C, plus the approximate weight of parts to be lifted for un-tanking, type and quantity of oil, and the date of manufacture.

    - A non-corrosive nameplate located next to the operating handle of the de-energized tap changer shall be provided which states the following: ‘Warning - Do not operate this tap changer unless the transformer is de-energized.”

  - Exterior Finish

    - The transformer exterior painting system shall be the manufactures standard. However, as a minimum, the transformer shall be thoroughly cleaned and phosphortized, painted with at least one corrosion inhibiting primer and one finish coat to provide a minimum total dry-film thickness of not less than 3 mils.

    - The finish shall be {ANSI 61} {ANSI 24} {OTHER _______}.

  - Testing

    - Each transformer shall receive all standard routine tests as required by ANSI C57.12.00 and performed as specified by ANSI C57.12.90.

    - Optional tests, as indicated on the Transformer Data Sheet, will also be required.

    - A certified test report shall be submitted and shall contain the test data for each transformer serial number manufactured. The certified test report shall as a minimum contain the data as specified in ANSI C57.12.90.

    - Short Circuit withstand capability shall be verified by full short circuit tests on similar or larger units in accordance with the latest revision of ANSI C57.12.00 and ANSI C57.12.90.  The maximum allowable variation in impedance measured on a per-phase basis after the test series shall not differ from that measured before the test series by more than 2% for category II and III equipment for circular or noncircular coils.  Certified test reports from applicable short circuit tests shall be submitted to the purchaser, upon request, prior to shipment of the transformers.

    - All symbols and wiring identification systems shall be in accordance with the applicable ANSI standard.

- ENGINEERING DATA REQUIREMENTS

  - Drawing Requirements

    - The required drawing format is specified on the Transformer Data Sheet.

    - The outline drawings shall be completely dimensioned and, as a minimum, show the following:

a.	Plan, and all elevations, including clearance for bushing and core and coil removal.

- High voltage and low voltage bushing details.

- Location of all handholes.

- Location and identification of all accessories.

- Size and location of all conduit entrances for Buyers connections.

- Anchoring details.

- Ground pad locations.

- Weight of core and coil, transformer tank and fittings, weight and gallons of fluid, and total shipping weight.

    - Wiring diagrams

      - Detailed connection (wiring) diagrams shall show the following:

a.	Interconnecting wiring of all components of the forced cooling equipment.

b.	Wiring of all devices with switches and relays, or electrical connections, including current transformers.

C.	Identification of all terminal blocks and all connections to be made by Buyer.

    - Nameplate drawing

      - A nameplate drawing showing required ANSI information shall be provided.

- Installation, Operating, and Maintenance Instructions

  - The seller shall provide an instruction, operating and maintenance manual covering all equipment furnished.

- Parts

  - The Seller shall provide a renewal parts list to the Buyer.